## Wills St WWTP results template
WILLS STREET WASTEWATER TREATMENT PLANT
Licensee: | Essential Energy (trading as Essential Water)
Licensee Address: | P.O Box 718, QUEANBEYAN, NSW 2620
Facility Address: | Lot 100 DP 1136508, Wills Street, BROKEN HILL NSW 2880
Environmental Protection Licence Number: | 3925
Scheduled Activity: | Sewerage Treatment
Sample date: | 2022-09-13
Sampled by: | Terry Sayers
Data obtained: | 2022-09-27
Date published: | (insert)
Concentration Limits:
Sampling Point (EPA Identification No:) | Monitoring frequency required by licence: | Pollutant: | Measurement: | Licence Limit: | Unit: | Sampling Method:
6 | Special Frequency 1# | Biochemical Oxygen Demand | 5 | 50 | Milligrams Per Litre | Special Method 1*
6 | Quarterly | Cadmium |  | N/A | Milligrams Per Litre | Representative sample
6 | N/A (refer notes)^ | Chlorophyll a | 6.68 | N/A | Micrograms per Litre | Representative sample
6 | N/A (refer notes)^ | Chlorophyll b | 0.33 | N/A | Micrograms per Litre | Representative sample
6 | Quarterly | Lead |  | N/A | Milligrams Per Litre | Representative sample
6 | Special Frequency 1# | Nitrate + Nitrite (oxidised nitrogen) |  | N/A | Milligrams Per Litre | Special Method 1*
6 | Special Frequency 1# | Oil and Grease |  | 10 | Milligrams Per Litre | Special Method 1*
6 | Quarterly | pH | 7.5 | 6.5 - 8.5 | pH | Representative sample
6 | Special Frequency 1# | Phosphorus (Total) |  | N/A | Milligrams Per Litre | Special Method 1*
6 | Special Frequency 1# | Total Dissolved Solids | 902 | N/A | Milligrams Per Litre | Special Method 1*
6 | Special Frequency 1# | Total Kjeldahl Nitrogen |  | N/A | Milligrams Per Litre | Special Method 1*
6 | Special Frequency 1# | Total Suspended Solids | 2 | 50 | Milligrams Per Litre | Special Method 1*
NOTES:
Special Frequency 1 # - means the collection of samples taken twelve (12) times per year at a minimum of 25 days apart
Special Method 1* - means the collection of a composite sample by taking at least three (3) grab samples forming the composite, with the first and last samples taken at least seven (7) hours apart
^Chlorophyll - Chlorophyll is not a sampling parameter required by the licence. It is monitored because the licensee if not taken to have exceeded a quality limit for Biochemical Oxygen demand, Total
suspended solids or pH if monitoring shows that the level of chlorophyll-a in the maturation ponds during any exceedance was 100 ug/L or more (showing that the exceedance was caused by algae growth).
Volume & Mass Limits:
Monitoring Point (EPA Identification No:) | Measurement: | Licence Volume/Mass Limit | Unit: | Frequency: | Sampling methods:
2 | 3182 | 18150 | kilolitres per day (kL/d) | Continuous | Level sensor & continuous logger
Notes & Licence Limit Exceedances:
(Insert details of any exceedances, problems with equipment or sampling etc here)