## South WWTP results template
SOUTH WASTEWATER TREATMENT PLANT
Licensee: | Essential Energy (trading as Essential Water)
Licensee Address: | P.O Box 5730, PORT MACQUARIE, NSW 2444
Facility Address: | Lot 1 DP 767329, Picton Street, BROKEN HILL NSW 2880
Environmental Protection Licence Number: | 5067
Scheduled Activity: | Sewerage Treatment
Sample date: | 2025-08-12
Sampled by: | Terry Sayer
Data obtained: | 2025-11-18
Date published: | 2026-02-02
Concentration Limits:
Sampling Point (EPA Identification No): | Monitoring frequency required by licence: | Pollutant: | Measurement: | Licence Limit: | Unit: | Sampling Method:
9 | Quarterly | Biochemical Oxygen Demand | 3 | 50 | Milligrams Per Litre | Grab Sample
9 | Quarterly | Cadmium | 0.0001 | N/A | Milligrams Per Litre | Grab Sample
9 | N/A (Refer to notes)^ | Chlorophyll a | 4.51 | N/A | Micrograms Per Litre | Grab Sample
9 | N/A (Refer to notes)^ | Chlorophyll b | 1.09 | N/A | Micrograms Per Litre | Grab Sample
9 | Quarterly | Lead | 0.003 | N/A | Milligrams Per Litre | Grab Sample
9 | Quarterly | Nitrate + Nitrite (oxidised nitrogen) | 14.78 | N/A | Milligrams Per Litre | Grab Sample
9 | Quarterly | Oil and Grease | 4 | 10 | Milligrams Per Litre | Grab Sample
9 | Quarterly | pH | 7.7 | 6.5 - 8.5 | pH | Grab Sample
9 | Quarterly | Phosphorus (Total) | 6.59 | N/A | Milligrams Per Litre | Grab Sample
9 | Quarterly | Total Dissolved Solids | 439 | N/A | Milligrams Per Litre | Grab Sample
9 | Quarterly | Total Kjeldahl Nitrogen | 8.64 | N/A | Milligrams Per Litre | Grab Sample
9 | Quarterly | Total Suspended Solids | 3 | 50 | Milligrams Per Litre | Grab Sample
9 | Quarterly | Faecal Coliforms | 20 | 600 | Colony Forming Units Per 100 Millilitres | Grab Sample
NOTES:
^Chlorophyll - Chlorophyll is not a sampling parameter required by the licence. It is monitored because the licensee if not taken to have exceeded a quality limit for Biochemical Oxygen demand, Total
suspended solids or pH if monitoring shows that the level of chlorophyll-a in the maturation ponds during any exceedance was 100 ug/L or more (showing that the exceedance was caused by algae growth).
Volume & Mass Limits:
Monitoring Point (EPA Identification No:) | Measurement: | Licence Volume/Mass Limit | Unit: | Frequency: | Sampling methods:
10 | 965 | 3628 | kilolitres per day (kL/d) | Continuous | Flow meter and continuous logger
Notes & Licence Limit Exceedances